## Project
Value
Project ID | 02040180PM
Spec #
Inspection Date | 2003-05-13
Inspection Type | Semi-Annual
Technicians | Clyde Fairbanks, Gene McGirl
Customer | ACME Banking
Contact | John Smith
Phone | 555-555-5555
Address | 325 Grand Blvd.
City | New York
State | NY
Zip | 12345
Site | ACME Banking
Contact | John Smith
Phone | 555-555-5555
Address | 325 Grand Blvd.
City | New York
State | NY
Zip | 12345

## System
Value
System ID | 20 KVA UPS
Spec #
Rectifier Type | 3Ø UPS
# Rectifiers/UPS | 1
# Strings | 1
# Units per String | 180
Max String Current | 92.6 Amps
OCP Type | Breaker
OCP Rating | 100 Amps
Ambient Temp. | 79 °F
Charge State | Float
Battery Rack | EP-Stack
Module Orientation | Normal
Cell Labeling | Cell 1 Most Positive
Internal Ohmic Meter | Cellcorder

## Modeling
Value
Battery Manufacturer | GNB
Battery Model | 90A09
Battery Type | VR-AGM
Battery Ah Rating | 350 Ah @ 8Hr. rate to 1.75vpc
# Cells Per Unit | 1
Min Ambient Temp. | 65
Max Ambient Temp. | 80
Nom Cell Voltage | 2.25
Min Cell Voltage | 2.23
Max Cell Voltage | 2.27
Voltage Temp. Corr. | 0.003
Nom Specific Gravity | -
Specific Gravity Flag
Internal Ohmic Type | Resistance
Nom Int. Ohmic Value | 689
Internal Ohmic Scale | uOhms
Internal Ohmic Flag | 20%
Max inter-cell drop | 30 mV
Max inter-tier drop | 100 mV
Inter-cell Baseline
Inter-tier Baseline

## Visual
| Evaluation | Comment
Safety Placards | ok
Eye-wash/Shower | ok
Ventilation | ok
Fire Suppression | not ok | No fire extinguisher present.
Spill Containment | n/a
Frame Ground | not ok | None.
Electrolyte Level | n/a
Posts | ok
Connections | ok
Valves/Arrestors | ok
Catalyst | n/a
Rack/Cabinet | ok
Covers | ok
Jars | ok
External Post Seals | ok
Internal Post Seals | n/a
Positive Plates | n/a
Negative Plates | n/a
Sediment | n/a
Torque | ok
Load Test | n/a
Insulation Test | n/a
Cell Pressure Test | n/a
Thermography Test | n/a

## Rectifiers
UPS ID | Spec. # | Manufacturer | Model | Serial Number | Rating | Meter Vdc | Meter Adc
UPS 1 | UDC63020C25DT03 | Liebert | AP332 | M11950F | 20 Kva | 405 | 0.01

## Strings
String ID | Spec. # | Install Date | String Vac | P-Gnd Vac | N-Gnd Vac | String Aac | String Vdc | P-Gnd Vdc | N-Gnd Vdc | String Adc | P-Term R | N-Term R
String 1 |  | 1999-10-01 | 0.37 | 81.8 | 31.06 | 2.98 | 405 | 201.7 | 202.8 | 0.4 | na | na

## Cells
Cell ID | Serial Number | Date Code | Voltage | + Electrode | - Electrode | uOhms | Gravity | Temperature | Rconn-A | Rconn-B | Rconn-C
String 1 - Cell 1 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 574 |  | 80 | 54
String 1 - Cell 2 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 574 |  | 80 | 58
String 1 - Cell 3 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 574 |  | 80 | 54
String 1 - Cell 4 | KEB12A099 | 1999-05-01 | 2.26 |  |  | 587 |  | 80 | 56
String 1 - Cell 5 | KEB12A099 | 1999-05-01 | 2.26 |  |  | 600 |  | 80 | 55
String 1 - Cell 6 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 574 |  | 80 | 55
String 1 - Cell 7 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 587 |  | 80 | 36
String 1 - Cell 8 | KEB12A099 | 1999-05-01 | 2.26 |  |  | 587 |  | 80 | 58
String 1 - Cell 9 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 613 |  | 80 | 59
String 1 - Cell 10 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 574 |  | 80 | 56
String 1 - Cell 11 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 600 |  | 80 | 58
String 1 - Cell 12 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 561 |  | 80 | 55
String 1 - Cell 13 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 561 |  | 80 | 58
String 1 - Cell 14 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 600 |  | 80 | 39
String 1 - Cell 15 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 600 |  | 80 | 54
String 1 - Cell 16 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 600 |  | 80 | 55
String 1 - Cell 17 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 581 |  | 80 | 56
String 1 - Cell 18 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 580 |  | 80 | 58
String 1 - Cell 19 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 580 |  | 80 | 55
String 1 - Cell 20 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 613 |  | 80 | 58
String 1 - Cell 21 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 587 |  | 80 | 40
String 1 - Cell 22 | KEB12A099 | 1999-05-01 | 2.26 |  |  | 574 |  | 80 | 59
String 1 - Cell 23 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 574 |  | 80 | 60
String 1 - Cell 24 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 600 |  | 80 | 57
String 1 - Cell 25 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 574 |  | 80 | 58
String 1 - Cell 26 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 574 |  | 80 | 57
String 1 - Cell 27 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 607 |  | 80 | 60
String 1 - Cell 28 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 587 |  | 80 | 40
String 1 - Cell 29 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 613 |  | 80 | 56
String 1 - Cell 30 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 567 |  | 80 | 56
String 1 - Cell 31 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 567 |  | 80 | 53
String 1 - Cell 32 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 594 |  | 80 | 57
String 1 - Cell 33 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 574 |  | 80 | 55
String 1 - Cell 34 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 608 |  | 80 | 55
String 1 - Cell 35 | KEB12A099 | 1999-05-01 | 2.26 |  |  | 600 |  | 80 | 38
String 1 - Cell 36 | KEB12A099 | 1999-05-01 | 2.26 |  |  | 620 |  | 80 | 59
String 1 - Cell 37 | KEB12A099 | 1999-05-01 | 2.26 |  |  | 600 |  | 80 | 58
String 1 - Cell 38 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 607 |  | 80 | 61
String 1 - Cell 39 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 600 |  | 80 | 54
String 1 - Cell 40 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 567 |  | 80 | 59
String 1 - Cell 41 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 594 |  | 80 | 59
String 1 - Cell 42 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 610 |  | 80 | 776 IT
String 1 - Cell 43 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 548 |  | 80 | 54
String 1 - Cell 44 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 633 |  | 80 | 56
String 1 - Cell 45 | KEB12A099 | 1999-05-01 | 2.26 |  |  | 574 |  | 80 | 57
String 1 - Cell 46 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 548 |  | 80 | 55
String 1 - Cell 47 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 561 |  | 80 | 58
String 1 - Cell 48 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 548 |  | 80 | 56
String 1 - Cell 49 | KEB12A099 | 1999-05-01 | 2.26 |  |  | 626 |  | 80 | 38
String 1 - Cell 50 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 574 |  | 80 | 61
String 1 - Cell 51 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 575 |  | 80 | 63
String 1 - Cell 52 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 581 |  | 80 | 57
String 1 - Cell 53 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 594 |  | 80 | 56
String 1 - Cell 54 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 554 |  | 80 | 57
String 1 - Cell 55 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 620 |  | 80 | 60
String 1 - Cell 56 | KEB12A099 | 1999-05-01 | 2.24 |  |  | 567 |  | 80 | 42
String 1 - Cell 57 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 580 |  | 80 | 56
String 1 - Cell 58 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 580 |  | 80 | 56
String 1 - Cell 59 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 555 |  | 80 | 58
String 1 - Cell 60 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 561 |  | 80 | 55
String 1 - Cell 61 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 608 |  | 80 | 56
String 1 - Cell 62 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 647 |  | 80 | 54
String 1 - Cell 63 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 587 |  | 80 | 37
String 1 - Cell 64 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 607 |  | 80 | 59
String 1 - Cell 65 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 607 |  | 80 | 60
String 1 - Cell 66 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 548 |  | 80 | 61
String 1 - Cell 67 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 541 |  | 80 | 60
String 1 - Cell 68 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 594 |  | 80 | 59
String 1 - Cell 69 | KEB12A099 | 1999-05-01 | 2.24 |  |  | 580 |  | 80 | 63
String 1 - Cell 70 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 594 |  | 80 | 38
String 1 - Cell 71 | KEB12A099 | 1999-05-01 | 2.24 |  |  | 568 |  | 80 | 55
String 1 - Cell 72 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 607 |  | 80 | 60
String 1 - Cell 73 | KEB12A099 | 1999-05-01 | 2.27 |  |  | 522 |  | 80 | 57
String 1 - Cell 74 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 574 |  | 80 | 58
String 1 - Cell 75 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 561 |  | 80 | 56
String 1 - Cell 76 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 574 |  | 80 | 56
String 1 - Cell 77 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 613 |  | 80 | 36
String 1 - Cell 78 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 580 |  | 80 | 59
String 1 - Cell 79 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 600 |  | 80 | 56
String 1 - Cell 80 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 561 |  | 80 | 58
String 1 - Cell 81 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 541 |  | 80 | 61
String 1 - Cell 82 | KEB12A099 | 1999-05-01 | 2.24 |  |  | 555 |  | 80 | 58
String 1 - Cell 83 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 594 |  | 80 | 59
String 1 - Cell 84 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 581 |  | 80 | 46 IT
String 1 - Cell 85 | KEB12A099 | 1999-05-01 | 2.24 |  |  | 568 |  | 80 | 54
String 1 - Cell 86 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 567 |  | 80 | 58
String 1 - Cell 87 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 594 |  | 80 | 57
String 1 - Cell 88 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 548 |  | 80 | 57
String 1 - Cell 89 | KEB12A099 | 1999-05-01 | 2.26 |  |  | 562 |  | 80 | 57
String 1 - Cell 90 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 594 |  | 80 | 56
String 1 - Cell 91 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 600 |  | 80 | 39
String 1 - Cell 92 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 607 |  | 80 | 59
String 1 - Cell 93 | KEB12A099 | 1999-05-01 | 2.24 |  |  | 581 |  | 80 | 59
String 1 - Cell 94 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 574 |  | 80 | 59
String 1 - Cell 95 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 567 |  | 80 | 61
String 1 - Cell 96 | KEB12A099 | 1999-05-01 | 2.24 |  |  | 574 |  | 80 | 59
String 1 - Cell 97 | KEB12A099 | 1999-05-01 | 2.24 |  |  | 548 |  | 80 | 59
String 1 - Cell 98 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 574 |  | 80 | 39
String 1 - Cell 99 | KEB12A099 | 1999-05-01 | 2.24 |  |  | 580 |  | 80 | 53
String 1 - Cell 100 | KEB12A099 | 1999-05-01 | 2.24 |  |  | 594 |  | 80 | 57
String 1 - Cell 101 | KEB12A099 | 1999-05-01 | 2.24 |  |  | 554 |  | 80 | 56
String 1 - Cell 102 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 548 |  | 80 | 56
String 1 - Cell 103 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 554 |  | 80 | 54
String 1 - Cell 104 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 594 |  | 80 | 53
String 1 - Cell 105 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 561 |  | 80 | 38
String 1 - Cell 106 | KEB12A099 | 1999-05-01 | 2.28 |  |  | 573 |  | 80 | 57
String 1 - Cell 107 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 594 |  | 80 | 61
String 1 - Cell 108 | KEB12A099 | 1999-05-01 | 2.24 |  |  | 554 |  | 80 | 58
String 1 - Cell 109 | KEB12A099 | 1999-05-01 | 2.24 |  |  | 580 |  | 80 | 61
String 1 - Cell 110 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 535 |  | 80 | 58
String 1 - Cell 111 | KEB12A099 | 1999-05-01 | 2.24 |  |  | 581 |  | 80 | 62
String 1 - Cell 112 | KEB12A099 | 1999-05-01 | 2.24 |  |  | 568 |  | 80 | 40
String 1 - Cell 113 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 574 |  | 80 | 54
String 1 - Cell 114 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 567 |  | 80 | 53
String 1 - Cell 115 | KEB12A099 | 1999-05-01 | 2.26 |  |  | 522 |  | 80 | 56
String 1 - Cell 116 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 535 |  | 80 | 59
String 1 - Cell 117 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 561 |  | 80 | 52
String 1 - Cell 118 | KEB12A099 | 1999-05-01 | 2.24 |  |  | 594 |  | 80 | 57
String 1 - Cell 119 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 594 |  | 80 | 41
String 1 - Cell 120 | KEB12A099 | 1999-05-01 | 2.28 |  |  | 613 |  | 80 | 59
String 1 - Cell 121 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 561 |  | 80 | 57
String 1 - Cell 122 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 554 |  | 80 | 58
String 1 - Cell 123 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 581 |  | 80 | 57
String 1 - Cell 124 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 528 |  | 80 | 59
String 1 - Cell 125 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 568 |  | 80 | 59
String 1 - Cell 126 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 567 |  | 80 | 48 IT
String 1 - Cell 127 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 567 |  | 80 | 55
String 1 - Cell 128 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 594 |  | 80 | 58
String 1 - Cell 129 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 574 |  | 80 | 57
String 1 - Cell 130 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 574 |  | 80 | 56
String 1 - Cell 131 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 574 |  | 80 | 58
String 1 - Cell 132 | KEB12A099 | 1999-05-01 | 2.26 |  |  | 541 |  | 80 | 53
String 1 - Cell 133 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 570 |  | 80 | 41
String 1 - Cell 134 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 621 |  | 80 | 60
String 1 - Cell 135 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 561 |  | 80 | 61
String 1 - Cell 136 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 548 |  | 80 | 57
String 1 - Cell 137 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 535 |  | 80 | 59
String 1 - Cell 138 | KEB12A099 | 1999-05-01 | 2.24 |  |  | 580 |  | 80 | 57
String 1 - Cell 139 | KEB12A099 | 1999-05-01 | 2.24 |  |  | 562 |  | 80 | 59
String 1 - Cell 140 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 561 |  | 80 | 40
String 1 - Cell 141 | KEB12A099 | 1999-05-01 | 2.26 |  |  | 561 |  | 80 | 58
String 1 - Cell 142 | KEB12A099 | 1999-05-01 | 2.24 |  |  | 607 |  | 80 | 56
String 1 - Cell 143 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 548 |  | 80 | 55
String 1 - Cell 144 | KEB12A099 | 1999-05-01 | 2.24 |  |  | 554 |  | 80 | 58
String 1 - Cell 145 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 587 |  | 80 | 56
String 1 - Cell 146 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 561 |  | 80 | 58
String 1 - Cell 147 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 613 |  | 80 | 39
String 1 - Cell 148 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 633 |  | 80 | 60
String 1 - Cell 149 | KEB12A099 | 1999-05-01 | 2.24 |  |  | 567 |  | 80 | 59
String 1 - Cell 150 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 541 |  | 80 | 58
String 1 - Cell 151 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 535 |  | 80 | 60
String 1 - Cell 152 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 574 |  | 80 | 57
String 1 - Cell 153 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 574 |  | 80 | 59
String 1 - Cell 154 | KEB12A099 | 1999-05-01 | 2.26 |  |  | 574 |  | 80 | 39
String 1 - Cell 155 | KEB12A099 | 1999-05-01 | 2.26 |  |  | 554 |  | 80 | 58
String 1 - Cell 156 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 587 |  | 80 | 57
String 1 - Cell 157 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 535 |  | 80 | 56
String 1 - Cell 158 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 548 |  | 80 | 56
String 1 - Cell 159 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 548 |  | 80 | 56
String 1 - Cell 160 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 561 |  | 80 | 56
String 1 - Cell 161 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 626 |  | 80 | 39
String 1 - Cell 162 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 600 |  | 80 | 56
String 1 - Cell 163 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 594 |  | 80 | 60
String 1 - Cell 164 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 567 |  | 80 | 59
String 1 - Cell 165 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 567 |  | 80 | 60
String 1 - Cell 166 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 561 |  | 80 | 59
String 1 - Cell 167 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 581 |  | 80 | 62
String 1 - Cell 168 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 594 |  | 80 | 59
String 1 - Cell 169 | KEB12A099 | 1999-05-01 | 2.24 |  |  | 567 |  | 80 | 40
String 1 - Cell 170 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 567 |  | 80 | 41
String 1 - Cell 171 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 580 |  | 80 | 40
String 1 - Cell 172 | KEB12A099 | 1999-05-01 | 2.24 |  |  | 581 |  | 80 | 41
String 1 - Cell 173 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 567 |  | 80 | 41
String 1 - Cell 174 | KEB12A099 | 1999-05-01 | 2.24 |  |  | 580 |  | 80 | 46 IT
String 1 - Cell 175 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 554 |  | 80 | 39
String 1 - Cell 176 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 567 |  | 80 | 41
String 1 - Cell 177 | KEB12A099 | 1999-05-01 | 2.24 |  |  | 580 |  | 80 | 41
String 1 - Cell 178 | KEB12A099 | 1999-05-01 | 2.24 |  |  | 608 |  | 80 | 42
String 1 - Cell 179 | KEB12A099 | 1999-05-01 | 2.24 |  |  | 561 |  | 80 | 40
String 1 - Cell 180 | KEB12A099 | 1999-05-01 | 2.25 |  |  | 542 |  | 80 | 19
Averages
| - | - | Voltage | + Electrode | - Electrode | uOhms | Gravity | Temperature | Inter-Cell R | IT/IR/SH/SW R
Average |  |  | 2.25 |  |  | 577 |  | 80 | 54.1 | 229
Minimum |  |  | 2.24 |  |  | 522 |  | 80 | 19 | 46
Maximum |  |  | 2.28 |  |  | 647 |  | 80 | 63 | 776

## Evaluation
Summary
We recommend that Cat-vents be installed. No other corrective action recommended at this time.
Recommendations
VISUAL: See 'Visual Inspection' section of this report. COMMENT: Safety equipment requirements should be reviewed COMMENT: Battery frames should be grounded. COMMENT: Cell 88 had dried acid on the top side of the jar cover. Area was cleaned and neutralized. This cell passed pressure test. CELL VOLTAGE: String 1, Cells; 73, 106, 120. COMMENT: Cell voltages are a slightly high but within acceptable tolerance. No corrective action is required at this time. Batteries should be monitored semi-annually.